## Sheet1
Requirements
Req ID | Requirement Title | Requirement Intent
ACC-REQ-001 | System Initialization | On system start, the controller shall enter the Power_Off with compressor_on = 0, fan_on = 0, fault_indicator = 0, and status outputs reset.
ACC-REQ-002 | Temperature Setpoint Input | The controller shall use set_temperature as the desired room temperature reference for cooling control.
ACC-REQ-003 | Power ON Command | When power_button == 1, the controller shall enter the enabled operating state, compute temperature_error = room_temperature - set_temperature, and determine cooling demand based on temperature_error and temperature_hysteresis_band.
ACC-REQ-004 | Power OFF Command | When power_button == 0, the controller shall enter the Power_Off state and set compressor_on = 0 and fan_on = 0.
ACC-REQ-005 | Cooling Demand Activation | If temperature_error >= temperature_hysteresis_band, the controller shall set cooling_demand = 1.
ACC-REQ-006 | Cooling Demand Deactivation | If temperature_error <= -temperature_hysteresis_band, the controller shall set cooling_demand = 0.
ACC-REQ-007 | Compressor Minimum OFF Time | After the compressor turns OFF, the controller shall prevent compressor restart until compressor_min_off_time has elapsed.
ACC-REQ-008 | Compressor Activation | If cooling_demand == 1 and the compressor is not in minimum-OFF-time lockout, the controller shall set compressor_on = 1.
ACC-REQ-009 | Compressor Deactivation | If cooling_demand == 0, power_button == 0, or a fault condition is active, the controller shall set compressor_on = 0.
ACC-REQ-010 | Fan Activation During Compressor Activation | When compressor_on == 1, the controller shall set fan_on = 1.
ACC-REQ-011 | Fan Behavior After Compressor Deactivation | When compressor_on == 0 after active cooling, the controller shall keep fan_on = 1 for configured fan_run_on_time, then set fan_on = 0.